## Energy Pulses (PL_constant)
Meter Constant = | 36964.5956
PL_constant (DEC) = | 12173811
PL_constant (HEX) = | 00B9C1F3
PLconstH = | 00B9
PLconstL = | C1F3
00B9
C1F3
00B9C1F3
12173811
| 36964.5956 | 36964.5956

## CT Selection & Load Resistance
PGA Gain Configuration
PGA_GAIN | Min | Max | Unit
1 | 0.12 | 720 | mVrms
2 | 0.07 | 360 | mVrms
4 | 0.04 | 180 | mVrms
CT Ratio | Rated Primary Current | Rated Secondary Current | Unit
| 200 | 5 | A
Selected PGA_GAIN | 1
Input Channels Configuration
| Min | Max | Unit
ADC Voltage | 0.12 | 720 | mVrms
Primary Current | 2 | 120 | A
Secondary Current | 0.05 | 3 | A
R1 & R2 | 0.0024 | 0.24 | Ohm
R1 & R2 Rated Power @MAX CT Current | 0.0216 | 2.16 | W
Output Parameters
Parameter | Value |  | Unit
Selected Load Resistance | 0.05 |  | Ohm
Rated Resistance Power | 0.45 |  | W
Sampling Channel | 2.5 | 150 | mVrms
28.5

## Voltage & Current Gain
R1 | 1680 | kOhm
R2 | 1 | kOhm
Reference Voltage | 220 | Vrms
Actual Measured Voltage | 220 | Vrms
Existing Gain | 52800 | CE40
Voltage Gain (To Set) | 52800 | CE40
Reference Current | 5 | Arms
Actual Measured Current | 5 | Arms
Existing Gain | 3000 | 0BB8
Current Gain (To Set) | 3000 | 0BB8
Voltage Threshold | 90 | %
SagTh Register | 39 | 0027

## Start
Name | Description | Address | Usage/Value |  |  | b15 | b14 | b13 | b12 | b11 | b10 | b9 | b8 | b7 | b6 | b5 | b4 | b3 | b2 | b1 | b0
ConfigStart | Configuration Reg. | 30H | Power up | Calibration | Operation | DNP
|  |  | 0x6886 | 0x5678 | 0x8765
PLconstH | High Word Energy Pulses | 31H | 0x00B9 |  |  | DNP
PLconstL | Low Word Energy Pulses | 32H | 0xC1F3 |  |  | DNP
MMode0 | Metering Method | 33H | 0x1087 |  |  | - | - | I1I3Swap | Freq60Hz | HPFOff | didtEn | 001LSB | 3P3W | CF2varh | CS2ESV | - | ABSEnQ | ABSEnP | EnPA | EnPB | EnPC
[6 empty] | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1
MMode1 | PGA Configuration | 34H | 0x0000 |  |  | DPGA_GAIN |  | PGA_GAIN (V3) |  | PGA_GAIN (V2) |  | PGA_GAIN (V1) |  | PGA_GAIN (I4) |  | PGA_GAIN (I3) |  | PGA_GAIN (I2) |  | PGA_GAIN (I1)
[6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PStartTh | Active Startup Power | 35H | 0x0001 |  |  | DNP
[6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
QStartTh | Reactive Startup Power | 36H | 0x0001 |  |  | DNP
[6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
SStartTh | Apparent Startup Power | 37H | 0x0001 |  |  | DNP
[6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
PPhaseTh | Startup Power Threshold | 38H | 0x0001 |  |  | DNP
[6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
QPhaseTh | Startup Power Threshold | 39H | 0x0001 |  |  | DNP
[6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
SPhaseTh | Startup Power Threshold | 3AH | 0x0001 |  |  | DNP
[6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
CSZero | Checksum Zero | 3BH | 0x1C0A |  |  | DNP
[5 empty] | HIGH WORD |  | LOW WORD
Checksum Computation |  | HEX | BIN | DEC | XOR |  | MOD
H31 | High Byte | 00 | 00000000 | 0 |  | 1C | 0A
H32 | High Byte | C1 | 11000001 | 193 | 1000001
H33 | High Byte | 10 | 00010000 | 16 | 1010001
H34 | High Byte | 00 | 00000000 | 0 | 1010001
H35 | High Byte | 00 | 00000000 | 0 | 1010001
H36 | High Byte | 00 | 00000000 | 0 | 1010001
H37 | High Byte | 00 | 00000000 | 0 | 1010001
H38 | High Byte | 00 | 00000000 | 0 | 1010001
H39 | High Byte | 00 | 00000000 | 0 | 1010001
H3A | High Byte | 00 | 00000000 | 0 | 1010001
L31 | Low Byte | B9 | 10111001 | 185 | 1101000
L32 | Low Byte | F3 | 11110011 | 243 | 0011011
L33 | Low Byte | 87 | 10000111 | 135 | 0011100
L34 | Low Byte | 00 | 00000000 | 0 | 11100
L35 | Low Byte | 01 | 00000001 | 1 | 11101
L36 | Low Byte | 01 | 00000001 | 1 | 11100
L37 | Low Byte | 01 | 00000001 | 1 | 11101
L38 | Low Byte | 01 | 00000001 | 1 | 11100
L39 | Low Byte | 01 | 00000001 | 1 | 11101
L3A | Low Byte | 01 | 00000001 | 1 | 11100

## Energy Calibration
Name | Description | Address | Usage/Value |  |  | b15 | b14 | b13 | b12 | b11 | b10 | b9 | b8 | b7 | b6 | b5 | b4 | b3 | b2 | b1 | b0
CalStart | Calibration Start | 40H | Power up | Calibration | Operation | DNP
|  |  | 0x6886 | 0x5678 | 0x8765
POffsetA | Phase A Offset (P) | 41H | 0x0000 |  |  | DNP
[6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QOffsetA | Phase A Offset (Q) | 42H | 0x0000 |  |  | DNP
[6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
POffsetB | Phase B Offset (P) | 43H | 0x0000 |  |  | DNP
[6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QOffsetB | Phase B Offset (Q) | 44H | 0x0000 |  |  | DNP
[6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
POffsetC | Phase C Offset (P) | 45H | 0x0000 |  |  | DNP
[6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QOffsetC | Phase C Offset (Q) | 46H | 0x0000 |  |  | DNP
[6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
GainA | Phase A Energy Gain | 47H | 0x0000 |  |  | DNP
[6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PhiA | Phase A Angle | 48H | 0x0000 |  |  | DNP
[6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
GainB | Phase B Energy Gain | 49H | 0x0000 |  |  | DNP
[6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PhiB | Phase A Angle | 4AH | 0x0000 |  |  | DNP
[6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
GainC | Phase C Energy Gain | 4BH | 0x0000 |  |  | DNP
[6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PhiC | Phase C Angle | 4CH | 0x0000 |  |  | DNP
[6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CS1 | Checksum 1 | 4DH | 0x0000 |  |  | DNP
[6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | HIGH WORD |  | LOW WORD
Checksum Computation |  | HEX | BIN | DEC | XOR |  | MOD
H41 | High Byte | 00 | 00000000 | 0 |  | 00 | 00
H42 | High Byte | 00 | 00000000 | 0 | 0
H43 | High Byte | 00 | 00000000 | 0 | 0
H44 | High Byte | 00 | 00000000 | 0 | 0
H45 | High Byte | 00 | 00000000 | 0 | 0
H46 | High Byte | 00 | 00000000 | 0 | 0
H47 | High Byte | 00 | 00000000 | 0 | 0
H48 | High Byte | 00 | 00000000 | 0 | 0
H49 | High Byte | 00 | 00000000 | 0 | 0
H4A | High Byte | 00 | 00000000 | 0 | 0
H4B | High Byte | 00 | 00000000 | 0 | 0
H4C | High Byte | 00 | 00000000 | 0 | 0
L41 | Low Byte | 00 | 00000000 | 0 | 0
L42 | Low Byte | 00 | 00000000 | 0 | 0
L43 | Low Byte | 00 | 00000000 | 0 | 0
L44 | Low Byte | 00 | 00000000 | 0 | 0
L45 | Low Byte | 00 | 00000000 | 0 | 0
L46 | Low Byte | 00 | 00000000 | 0 | 0
L47 | Low Byte | 00 | 00000000 | 0 | 0
L48 | Low Byte | 00 | 00000000 | 0 | 0
L49 | Low Byte | 00 | 00000000 | 0 | 0
L4A | Low Byte | 00 | 00000000 | 0 | 0
L4B | Low Byte | 00 | 00000000 | 0 | 0
L4C | Low Byte | 00 | 00000000 | 0 | 0

## Harmonic Calibration
Name | Description | Address | Usage/Value |  |  | b15 | b14 | b13 | b12 | b11 | b10 | b9 | b8 | b7 | b6 | b5 | b4 | b3 | b2 | b1 | b0
HarmStart | Calibration Start | 50H | Power up | Calibration | Operation | DNP
|  |  | 0x6886 | 0x5678 | 0x8765
POffsetAF | Phase A F Power Offset | 51H | 0x0000 |  |  | DNP
[6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
POffsetBF | Phase B F Power Offset | 52H | 0x0000 |  |  | DNP
[6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
POffsetCF | Phase C F Power Offset | 53H | 0x0000 |  |  | DNP
[6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PGainAF | Phase A F Power Gain | 54H | 0x0000 |  |  | DNP
[6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PGainBF | Phase B F Power Gain | 55H | 0x0000 |  |  | DNP
[6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PGainCF | Phase C F Power Gain | 56H | 0x0000 |  |  | DNP
[6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CS2 | Checksum 2 | 57H | 0x0000 |  |  | DNP
[6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | HIGH WORD |  | LOW WORD
Checksum Computation |  | HEX | BIN | DEC | XOR |  | MOD
H51 | High Byte | 00 | 00000000 | 0 |  | 00 | 00
H52 | High Byte | 00 | 00000000 | 0 | 0
H53 | High Byte | 00 | 00000000 | 0 | 0
H54 | High Byte | 00 | 00000000 | 0 | 0
H55 | High Byte | 00 | 00000000 | 0 | 0
H56 | High Byte | 00 | 00000000 | 0 | 0
H57 | High Byte | 00 | 00000000 | 0 | 0
L51 | Low Byte | 00 | 00000000 | 0 | 0
L52 | Low Byte | 00 | 00000000 | 0 | 0
L53 | Low Byte | 00 | 00000000 | 0 | 0
L54 | Low Byte | 00 | 00000000 | 0 | 0
L55 | Low Byte | 00 | 00000000 | 0 | 0
L56 | Low Byte | 00 | 00000000 | 0 | 0
L57 | Low Byte | 00 | 00000000 | 0 | 0

## Measurement Calibration
| Name | Description | Address | Usage/Value |  |  | b15 | b14 | b13 | b12 | b11 | b10 | b9 | b8 | b7 | b6 | b5 | b4 | b3 | b2 | b1 | b0
| AdjStart | Measurement Startup | 60H | Power up | Calibration | Operation | DNP
CE40 |  |  |  | 0x6886 | 0x5678 | 0x8765
11001110 | UgainA | Phase A Voltage RMS Gain | 61H | 0x0000 |  |  | DNP
01000000 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| IgainA | Phase A Current RMS Gain | 62H | 0x0000 |  |  | DNP
0BB8 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
00001011 | UoffsetA | Phase A Voltage RMS Offset | 63H | 0x0000 |  |  | DNP
10111000 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| IoffsetA | Phase A Current RMS Offset | 64H | 0x0000 |  |  | DNP
[7 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| UgainB | Phase A Voltage RMS Gain | 65H | 0x0000 |  |  | DNP
[7 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| IgainB | Phase B Current RMS Gain | 66H | 0x0000 |  |  | DNP
[7 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| UoffsetB | Phase B Voltage RMS Offset | 67H | 0x0000 |  |  | DNP
[7 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| IoffsetB | Phase B Current RMS Offset | 68H | 0x0000 |  |  | DNP
[7 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| UgainC | Phase C Voltage RMS Gain | 69H | 0x0000 |  |  | DNP
[7 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| IgainC | Phase C Current RMS Gain | 6AH | 0x0000 |  |  | DNP
[7 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| UoffsetC | Phase C Voltage RMS Offset | 6BH | 0x0000 |  |  | DNP
[7 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| IoffsetC | Phase C Current RMS Offset | 6CH | 0x0000 |  |  | DNP
[7 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| IgainN | N Line Current RMS Gain | 6DH | 0x0000 |  |  | DNP
[7 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| IoffsetN | N Line Current RMS Offset | 6EH | 0x0000 |  |  | DNP
[7 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CS3 | Checksum 3 | 6FH | 0x0000 |  |  | DNP
[7 empty] | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1
[6 empty] | HIGH WORD |  | LOW WORD
| Checksum Computation |  | HEX | BIN | DEC | XOR |  | MOD
| H61 | High Byte | 00 | 00000000 | 0 |  | 00 | 00
| H62 | High Byte | 00 | 00000000 | 0 | 0
| H63 | High Byte | 00 | 00000000 | 0 | 0
| H64 | High Byte | 00 | 00000000 | 0 | 0
| H65 | High Byte | 00 | 00000000 | 0 | 0
| H66 | High Byte | 00 | 00000000 | 0 | 0
| H67 | High Byte | 00 | 00000000 | 0 | 0
| H68 | High Byte | 00 | 00000000 | 0 | 0
| H69 | High Byte | 00 | 00000000 | 0 | 0
| H6A | High Byte | 00 | 00000000 | 0 | 0
| H6B | High Byte | 00 | 00000000 | 0 | 0
| H6C | High Byte | 00 | 00000000 | 0 | 0
| H6D | High Byte | 00 | 00000000 | 0 | 0
| H6E | High Byte | 00 | 00000000 | 0 | 0
| L61 | Low Byte | 00 | 00000000 | 0 | 0
| L62 | Low Byte | 00 | 00000000 | 0 | 0
| L63 | Low Byte | 00 | 00000000 | 0 | 0
| L64 | Low Byte | 00 | 00000000 | 0 | 0
| L65 | Low Byte | 00 | 00000000 | 0 | 0
| L66 | Low Byte | 00 | 00000000 | 0 | 0
| L67 | Low Byte | 00 | 00000000 | 0 | 0
| L68 | Low Byte | 00 | 00000000 | 0 | 0
| L69 | Low Byte | 00 | 00000000 | 0 | 0
| L6A | Low Byte | 00 | 00000000 | 0 | 0
| L6B | Low Byte | 00 | 00000000 | 0 | 0
| L6C | Low Byte | 00 | 00000000 | 0 | 0
| L6D | Low Byte | 00 | 00000000 | 0 | 0
| L6E | Low Byte | 00 | 00000000 | 0 | 0